TECHNICAL SPECIFICATION TEXT – WLHP 200

Innova WLHP water-to-air heat pump without outdoor unit and without wall openings, consisting of:

- high-thickness galvanized sheet steel supporting structure with internal thermal and acoustic insulation, rear panel in soundproofing material;

- complete casing in oven-painted galvanized sheet steel with epoxy powder coating, front diffuser with adjustable louver and digital control panel;

- condensate collection trays in shock-resistant PVC;

- high-efficiency brazed copper water/refrigerant plate heat exchanger;

- internal copper-aluminum heat exchange coil with high-efficiency mechanically expanded fin pack, designed by Innova's technical department and optimized to ensure maximum air passage uniformity;

- high-efficiency twin rotary compressor with DC Inverter motor;

- tangential fan assembly in synthetic material with staggered blades (very low noise) with continuously modulating DC Inverter motor, mounted on EPDM anti-vibration supports (DC Inverter model);

- Digital control touchpad with and without WiFi module (ECA944II/EWF944II).

- Compatible with M7 series remote controls (EEB749 / EFB749) as accessories and free App (iOS/Android);

- Optional accessories: 2/3-way modulating valves, injection pump kit, condensate disposal kit.

WLHP 200 DC Inverter MODEL, for wall installation.

Cooling data with room air T 27 °C, R.H. 50%, loop T 30 °C

- Nominal cooling capacity: 1.12 kW;

- Power input in cooling mode: 0.20 kW;

- EER: 5.60;

- Nominal water flow rate in cooling mode: 270 L/h;

Heating data with room air T 20 °C, R.H. 38%, loop T 20 °C

- Nominal heating capacity: 1.27 kW;

- Power input in heating mode: 0.18 kW;

- COP: 7.06;

- Nominal water flow rate in heating mode: 222 L/h;

- Dimensions (L x H x D): 775 x 641 x 144 mm;

- Weight: 35 kg

TECHNICAL SPECIFICATION TEXT – WLHP 400

Innova WLHP water-to-air heat pump without outdoor unit and without wall openings, consisting of:

- high-thickness galvanized sheet steel supporting structure with internal thermal and acoustic insulation, rear panel in soundproofing material;

- complete casing in oven-painted galvanized sheet steel with epoxy powder coating, front diffuser with adjustable louver and digital control panel;

- condensate collection trays in shock-resistant PVC;

- high-efficiency brazed copper water/refrigerant plate heat exchanger;

- internal copper-aluminum heat exchange coil with high-efficiency mechanically expanded fin pack, designed by Innova's technical department and optimized to ensure maximum air passage uniformity;

- high-efficiency twin rotary compressor with DC Inverter motor;

- tangential fan assembly in synthetic material with staggered blades (very low noise) with continuously modulating DC Inverter motor, mounted on EPDM anti-vibration supports (DC Inverter model);

- Digital control touchpad with and without WiFi module (ECA944II/EWF944II).

- Compatible with M7 series remote controls (EEB749 / EFB749) as accessories and free App (iOS/Android);

- Optional accessories: 2/3-way modulating valves, injection pump kit, condensate disposal kit.

WLHP 400 DC Inverter MODEL, for wall installation.

Cooling data with room air T 27 °C, R.H. 50%, loop T 30 °C

- Nominal cooling capacity: 1.52 kW;

- Power input in cooling mode: 0.31 kW;

- EER: 4.90;

- Nominal water flow rate in cooling mode: 312 L/h;

Heating data with room air T 20 °C, R.H. 38%, loop T 20 °C

- Nominal heating capacity: 2.14 kW;

- Power input in heating mode: 0.34 kW;

- COP: 6.29;

- Nominal water flow rate in heating mode: 462 L/h;

- Dimensions (L x H x D): 975 x 641 x 144 mm;

- Weight: 40 kg

TECHNICAL SPECIFICATION TEXT – WLHP 600

Innova WLHP water-to-air heat pump without outdoor unit and without wall openings, consisting of:

- high-thickness galvanized sheet steel supporting structure with internal thermal and acoustic insulation, rear panel in soundproofing material;

- complete casing in oven-painted galvanized sheet steel with epoxy powder coating, front diffuser with adjustable louver and digital control panel;

- condensate collection trays in shock-resistant PVC;

- high-efficiency brazed copper water/refrigerant plate heat exchanger;

- internal copper-aluminum heat exchange coil with high-efficiency mechanically expanded fin pack, designed by Innova's technical department and optimized to ensure maximum air passage uniformity;

- high-efficiency twin rotary compressor with DC Inverter motor;

- tangential fan assembly in synthetic material with staggered blades (very low noise) with continuously modulating DC Inverter motor, mounted on EPDM anti-vibration supports (DC Inverter model);

- Digital control touchpad with and without WiFi module (ECA944II/EWF944II).

- Compatible with M7 series remote controls (EEB749 / EFB749) as accessories and free App (iOS/Android);

- Optional accessories: 2/3-way modulating valves, injection pump kit, condensate disposal kit.

WLHP 600 DC Inverter MODEL, for wall installation.

Cooling data with room air T 27 °C, R.H. 50%, loop T 30 °C

- Nominal cooling capacity: 2.59 kW;

- Power input in cooling mode: 0.47 kW;

- EER: 5.51;

- Nominal water flow rate in cooling mode: 540 L/h;

Heating data with room air T 20 °C, R.H. 38%, loop T 20 °C

- Nominal heating capacity: 3.03 kW;

- Power input in heating mode: 0.51 kW;

- COP: 5.94;

- Nominal water flow rate in heating mode: 720 L/h;

- Dimensions (L x H x D): 1225 x 641 x 144 mm;

- Weight: 45 kg

TECHNICAL SPECIFICATION TEXT – WLHP VERTICAL 400

Innova WLHP Vertical water-to-air heat pump without outdoor unit and without wall openings, designed for indoor vertical wall installation, consisting of:

- High-thickness galvanized sheet steel supporting structure, with internal thermal and acoustic insulation and soundproofed rear panel;

- Casing in galvanized sheet steel painted with scratch-resistant epoxy powder coating, aesthetic front panel and integrated control touchpad;

- High-efficiency brazed copper water/refrigerant plate heat exchanger;

- Internal copper-aluminum air heat exchanger with high-efficiency mechanically expanded fin pack, designed by Innova's technical department and optimized to ensure maximum air passage uniformity;

- High-efficiency Twin Rotary DC Inverter compressor, with eco-friendly R290 gas (GWP=3);

- Radial fan in reinforced plastic, lightweight and very quiet, with front air intake and upper and side air supply flow, equipped with continuously modulating DC Brushless motor, mounted on EPDM anti-vibration supports;

- Shock-resistant PVC condensate tray with integrated drain;

- Digital control touchpad with and without WiFi module (ECA944II/EWF944II).

- Compatible with M7 series remote controls (EEB749 / EFB749) as accessories and free App (iOS/Android);

- Optional accessories: 2/3-way modulating valves, injection pump kit, condensate disposal kit.

WLHP Vertical 400 DC Inverter MODEL, for wall installation.

Cooling data with room air T 27 °C, R.H. 50%, loop T 30 °C

- Nominal cooling capacity: 1.80 kW;

- Power input in cooling mode: 0.33 kW;

- EER: 5.45;

- Nominal water flow rate in cooling mode: 360 L/h;

Heating data with room air T 20 °C, R.H. 38%, loop T 20 °C

- Nominal heating capacity: 2.20 kW;

- Power input in heating mode: 0.30 kW;

- COP: 7.33;

- Nominal water flow rate in heating mode: 540 L/h;

- Dimensions (L x H x D): 550 x 1115 x 144 mm;

- Weight: 40 kg